## All Part - QA Assurance
| Site Name | Site Number |  | Project | Tower height
| No Site Yet | T123-2345 |  | project ref here | hight of structure here
| Site Type (New Site Build, Rooftop, Upgrade etc): |  |  | xxxxx
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
A | Shelter/Container /Equipment Room | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
A1 | Internal and external finish/paint of container/equipment room / outdoor RBS cabinet is according to the specification.
A2 | Equipment room / container / outdoor RBS cabinet is built according to the specification and orientated according to site drawings.
A3 | Brick work grouted neatly.
A4 | Roof, gutters and down pipes as per specification
A5 | Surface scratches were kept at a minimum and are touched up after with touch up paint
A6 | Securing of container feet / cabinet base to specification.
A7 | Securing of container stays.
A8 | Cable entry gland sealed to specification.
A9 | Container roof sealing / waterproofing.
A10 | Door and mechanism operational as per specification.
A11 | Base mounting frame sealed as per specification.
A12 | Damage free and clean floors sealed against walls.
A13 | Are switches & sockets properly fixed & functional?
A14 | Is the shelter grounded to grounding ring?
A15 | Is the cable tray properly installed and grounded?
A16 | Is the fire fighting system secured and correctly positioned?
A17 | Are equipment installed within the shelter as specified by BTS site layout?
A18 | General workmanship
B | Air-conditioning units | Yes | No | Observation and action |  | Pass | Fail | Yes | No
B1 | Are the air conditioning units correctly installed?
B2 | Are the Air conditioning units functional?
B3 | Is the Air conditioner System Alarm functional?
B4 | Are both Air conditioning units cooling?
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
B | Air-conditioning Units | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
B5 | Does the Air conditioning unit multi run temp functional?
B6 | Does the Air conditioning unit swap time functional?
B7 | Does the Air conditioning unit(1) come on when power is cut off from the Air conditioning unit(2) & vice versa?
B8 | Is the A/C Drain pipe fitted and secured?
B9 | Is the A/C Vandal proof installed?
B10 | Is the Equipment easily accessible for maintenance?
B11 | Is the Auto restart functioning?
B12 | Are the Air conditioning units labeled A/C 1 & A/C 2?
B13 | Condensation pipe installed and unobstructed off plinth
B14 | Units and wall entries are 100% sealed and secured.
B15 | General workmanship
C | Electrical Installations | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
C1 | Does the Internal and external DB positions comply with technical submission?
C2 | All burrs and wire off cuts removed?(Especially inside the BD and behind trunking covers)
C3 | Surge protection Installed as per Specification?
C4 | All terminations tight and secure
C5 | Are the plugs, switches and lights installed to specification and operational?
C6 | External 230 V AC security light installed and operational.
C7 | Are the Internal ducts/conduits neat with good joints?
C8 | Top navigation lights fitted and operational
C9 | Midway navigation lights fitted and operational
C10 | Is the cable routing through requisite sleeves?
C11 | Does the Internal and external DB positions comply with technical submission?
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
C | Electrical Installations | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
C12 | Is the AC cable buried to correct depth or feed in pipe where this is not possible.? minimum 600mm
C13 | Electrical earth accompanying the AC feed armored cable
C14 | AC feed cable is armored and of correct diameter
C15 | All Supply phases supply balanced?
C16 | Mains Fail relay wired and operational.
C17 | Check the connections between the power supply system and the system earth.
C18 | Utility Electrical Meter Cabinet installed to specifications, wired & fitted with Class 1 Lightning arrestor?
C19 | Does the Electrical wiring in AC DB comply to layout?
C20 | AC supply circuit breaker comply with local regulations and installation instructions.
C21 | No strain on the AC termination points in the system
C22 | Check that load cables are in line with site drawings and are correctly sized for the circuit breaker rating
C23 | Is the Voltage surge and lightning suppression devices properly installed, wired, and operational?
C24 | Are the AC Circuit breakers properly labeled ?
C25 | Is the Electrical schematic diagram and plan of Power route available?
C26 | General workmanship
D | Automatic Voltage Regulator |  |  | Observation and Action |  | Pass | Fail | Yes | No
D1 | Check for Damage
D2 | Check for dirt on the inside
D3 | Has 16mm Squared armored cable been used
D4 | Are All Connection Tight and secure
D5 | Are all displays normal
D6 | Has the AVR been Bolted down
D7 | Have the sleeves been sealed
D8 | Operation manuals and electrical drawings available on site
D9 | General workmanship.
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
E | TRANSFORMER |  |  | Observation and Action |  | Pass | Fail | Yes | No
E1 | Check for Damage
E2 | Check for dirt on the inside
E3 | Has armored cable been usedaccording to specs size?
E4 | Are All Connection Tight and secure
E5 | Are all displays normal
E6 | Has the Transformer been Bolted down
E7 | Have the sleeves been sealed
E8 | Operation manuals and electrical drawings available on site
E9 | General workmanship.
F | DC Power | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
F1 | Check the floor and wall fixing of the cabinet
F2 | Is the Rectifier shelter properly fixed without wobbling?
F3 | Earthing as per company req. & inline with local regulations
F4 | Check that the cables for the alarm extension are connected correctly.
F5 | Are Rectifier modules operational without alarm?
F6 | Is the Rectifier properly grounded to DC ground bus bar?
F7 | Are all connections tightened and labeled?
F8 | Is the Cabling properly terminated to AC DB?
F9 | Check that all cables are properly secured via cable ties
F10 | Check that the battery orientation is correct
F11 | Check that the battery cabling is connected properly
F12 | Middle inter-cell connectors mounted
F13 | Battery sense cabling properly connected
F14 | Is the Battery properly terminated to rectifier?
F15 | Are the Batteries without damage nor leakage?
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
F | DC Power | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
F16 | Is the Central supervision unit operational?
F17 | Green LED on Mains monitor on
F18 | Are all materials/equipment used of approved type?
G | Locks | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
G1 | Is Type supplied for container as specified?
G2 | Is Type supplied for Fence Gate as specified?
G3 | Is Type supplied for Generator as specified?
G4 | Is Type supplied for External DB as specified?
G5 | Is Type supplied for Access Gate as specified?
H | Safety(applicable to rooftop sites) | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
H1 | Has the Anchor points been Installed in the event that Ab-sailing is to be performed?
H2 | Are safety handrails installed where required?
H4 | Rooftop safety anchor points installed and certified for use.
H5 | Warning signs are present.
I | AMF Panel | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
I1 | Is the AMF Panel connected with inputs(Utility, Generator(s))?
I2 | Is the AMF Panel properly mounted?
I3 | Is the AMF functioning properly?
I4 | Is Battery voltage meter installed?
I5 | Is the Battery failure alarm readable?
I6 | Is the Fuel level readable?
I7 | Is the Empty Fuel level readable?
I8 | Is Failure to Start readable?
I9 | Is the Generator Running indication readable?
I10 | Is the Public Utility power supply indication readable?
I11 | Is the Voltage meter present, readable & indicates all phases on generator, and Public Utility mains?
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
I | AMF Panel | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
I12 | Is the Hours Run readable?
I13 | Is the Short Circuit and Overload Protection (MCB) installed, and readable?
I14 | Is the Short Circuit Protection (fuses) for sensors and control cables installed?
J | Generator | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
J1 | Double Generators with Dual AMF Panel?
J2 | Are the doors fitted with locks and latch?
J3 | Is Generator positioned & mounted as specified in drawing?
J4 | Earth Connections
J5 | Is the Exhaust system and silencer installed properly?
J6 | Air Filtration System
J7 | Is the External fuel tank stable, secured and positioned according to drawing?
J8 | Is the Base frame fuel tank fabrication & capacity as specified?
J9 | Is water separator installed with the fuel tank as specified?
J10 | Is Fuel level as specified ?Any leakage in the fuel system?
J11 | Is Lubrication Oil level & quality acceptable?
J12 | Is the Coolant levels & additives acceptable?
J13 | Is Polarity on batteries and wiring correct?
J14 | Any damage to the electrical Instrument?
J15 | Is the Equipment properly secured & insulated?
J16 | Are all electrical cables(Generator to ATS etc) connected and fixed?
J17 | Radiator and Alternator Guards
J18 | Is clock hour counter functional?
J19 | Is the engine speed stable?
J20 | Is Generator of the approved type?
J21 | General workmanship
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
K | Site Signage | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
K1 | Is the Site Identification and Warning Board fitted to approach side of site?
K2 | Does the Site Identification clearly indicate the site ID?
K3 | Is the RF Warning sign fitted to visible position on approach path of mast close to cat-ladder?
K4 | Is the International Electrical Warning sign fitted to external DB?
L | Earthing | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
L1 | Is exposed earth connections covered with Denzo Paste?
L2 | Is the Earthing installation compliant with Technical Submissions?
L3 | Correct materials are used according to specification.
L4 | Earthing is completed according to and within specification.
L5 | All earth systems connected at equipment room /container / outdoor RBS cabinet earth point.
L6 | Are the Earthing points connected as specified in the Technical Submissions?
L7 | Is the DC ground bus bar bonded to grounding ring?
L8 | Is the AC ground bus bar bonded to DC ground bar?
L9 | Is the External ground bus bar bonded to grounding ring?
L10 | Is Grounding as specified in the drawing?
L11 | Are Grounding conductors securely fastened?
L12 | Are Grounding conductors as specified ?Minimum conductor size requirement of 70mm2
L13 | Utility box & Isolation Transformer bonded to grounding ring?
L14 | Shelter body & fence corners bonded to grounding ring?
L15 | Generator & Fuel tank bonded to grounding ring?
L16 | Tower legs & Feeder ground bars bonded to grounding ring?
L17 | Are grounding points within the shelter properly tightened?
L18 | Are the grounding cables installed properly and tightened?
L19 | General workmanship
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
M | Lighting | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
M1 | Is the night & day sensor switch(photocell) installed & functional?
M2 | Is the lightning for inside the shelter installed and functional?
M3 | Is the lightning for emergency installed & functional?
N | GSM Antenna and Feeder Installation | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
N1 | Installation orientation (azimuth) & height as per specification
N2 | Antenna mounting secure
N3 | Booms/mounting poles secured and stabilized
N4 | Antenna mounting poles on rooftop are stayed.
N5 | Dressing & Bending radius of feeders is according to Technical Specifications.
N6 | Feeders clamped as per Tech. Submission
N7 | Waterproofing kits installed correctly
N8 | Feeders earthed as per Technical Submission
N9 | Termination and length of feeders inside equipment room/outdoor RBS cabinet as per specification.
N10 | Surge Protectors fitted
N11 | Cable trays leveled, and properly fixed
N | GSM Antenna and Feeder Installation | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
N12 | Jumper cables secured & waterproofed
N13 | Feeders are secured inside cable tray with feeder clamps
N14 | Feeder entry plate dressed and sealed
N15 | Power & ground connection done as per specification
N16 | Entry Plate & Cable tray supports securely fixed and correctly positioned
N17 | Cable tray bonding and earthing done on rooftops
N18 | Inspect feeder cables and record type
N19 | Weather proofing kits installed properly
N20 | Grounding kits installed properly
N21 | Nuts, bolts & supports properly installed and Tightened
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
O | Alarm System (Tested through to the Krone block) | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
O1 | Is the Smoke detector fixed securely in correct position as per specification?
O2 | Smoke detector tested & functional?
O3 | Is the Thermostat sensor fixed securely and in correct position?
O4 | Test Door alarm by verifying contact opening and closing
O5 | Alarm system mountings are correct, neat and tested?
O6 | Alarm system ducting is neat and as per specification
O7 | Fire extinguisher mounting being secure and in the correct position if required.
O8 | DF alarm box wired neatly and operational
O9 | Krone Frame and Krone Blocks are installed
O12 | DC Light operational 24V / 48V
O14 | Is the Movement Sensor installed & functional?
O15 | Are the Alarm sensors installed and functional?
O16 | Mains Failure
O17 | Mains on Load
O18 | Generator on load
O19 | Generator fail to start
O20 | Low fuel in Base tank
O21 | Low fuel in external tank
O22 | Change Over Fail/Fault on Generator
O23 | Low Oil pressure
O24 | Start Battery Charge
O25 | Over Speed
O26 | Alternator Faulty
O27 | Movement Sensor Alarm intruder
| CIVIL INSTALLATIONS |  |  |  |  | Status |  | Rectified
O | Alarm System (Tested through to the Krone block) | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
O28 | Fire Alarm Warning
O29 | Fire on Site/Smoke Detector
O30 | Rectifier Load Disconnect
O31 | Rectifier Low Voltage prompt
O32 | Rectifier Module fail
O33 | Air conditioner System Fail
O34 | High Temperature
O35 | Aviation Beacon Fault
O36 | No unaccounted alarms
O37 | General workmanship
Additional Comments
Main Contractor Representative
Names:
Sign:
Date:
This documentation is not intended for usage during site construction since a complete and more comprehensive documentation is available for such inspections. The above data is an extract from such document and is intended only for the assistance in identification of faults by the QA team of the main civil Site Contractor
| TOWER, PLINTHS & FENCE |  |  |  |  | Status |  | Rectified
P | Tower Civil Works | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
P1 | Has a wood float finish been applied, and satisfactory?
P2 | Has the 45 degree chamfering been applied and satisfactory?
P3 | Spot check that member sizes correlate with drawing. Check markings on members.
P4 | Random Check at least 10 bolt torque. Use 20% less than specified torque of bolt being checked. If more than 3 bolts fail then test fails.
P5 | Check for bolt accessibility for maintenance purposes.
P6 | Minimum thread protruding from any bolt after nuts are tightened is 2 full treads.
P7 | Galvanized bolts are fully coated on the head; nuts and protruding threads are painted cold galv paint if that tower is not painted
P8 | Tower is level and plumb.
P9 | No twist is visible. If visible then measure.
P10 | Inspect galvanizing for damage. Physical chips and cracks must be treated with cold galv or zinc spray. Blackened scuffmarks need not be treated.
P11 | Cat ladder is straight, secure and extends to the highest point of the tower.
P12 | Safety rings are installed as per specification.
P13 | Ladder rungs are spaced evenly.
P14 | Trapdoor is fitted and opens according to specification.
P15 | Platforms and crows nests have safety rails.
P16 | Foundations have smooth wood float finish.
P17 | Foundation excavation has been properly backfilled and compacted.
P18 | Tower grouting below flanges are done to specification.
P19 | Tower painted and accepted.
P20 | Lighting spike is fixed securely on the top of tower.
P21 | General workmanship.
| TOWER, PLINTHS & FENCE |  |  |  |  | Status |  | Rectified
Q | Generator Slab (Post Cast ) | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
Q1 | Generator plinth dimension as per specification.
Q2 | Plinth / pillars edges neat with no broken edges.
Q3 | Plinths / pillars are level.
Q4 | Expansion joints positioned and installed to specification.
Q1 | Has a Wood float finish been applied and satisfactory?
Q2 | Has the 45 degree chamfering been applied and is this satisfactory?
R | Container Slab ( Post Cast) | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
R1 | Has a Wood float finish been applied and satisfactory?
R2 | Has the 45 degree chamfering been applied and is this satisfactory?
S | Mast Construction | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
S1 | Is there any visible twist in the mast? If yes, state number and heights which they occur
S2 | Are the hold down bolt protrusions correct? 3 threads minimum over the double nut
S3 | Has the proper non-shrink grout been used to the correct thinness(At least 30mm)
S4 | Is the first 3 horizontal members level?
S5 | Has the platform been installed
S6 | Are the Feeder cable brackets installed correctly?
S7 | Has the Lightning spike been installed?
S8 | Are the Cat ladders and cages straight?
S9 | Has the bolts been torque according to technical submissions?
S10 | M 12 - Min 27 N.m - Max 30 N.m
S11 | M 16 - Min 68 N.m - Max 75 N.m
S12 | M 20 - Min 132 N.m - Max 147 N.m
S13 | M 24 - Min 228 N.m - Max 253 N.m
S14 | Has the mast been painted according to International DCA Specifications, of 7 bands, white and International orange?
S15 | Are the climbing ladder securely mounted and straight?
S16 | Is the fixation and orientation of platforms correct?
| TOWER, PLINTHS & FENCE |  |  |  |  | Status |  | Rectified
S | Mast Construction | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
S17 | Is there any visible damage to Tower?
S18 | Tower legs properly bonded to ground ring
S19 | Tower legs leveled & tower vertically aligned
S20 | Are the bolts painted according to their position on the mast?
S21 | Are all the Nicks and scratches touched up?
S22 | Is Trapdoor fitted and opens as specified?
S23 | Are safety rings installed as per specification?
S24 | Good Workmanship
[6 empty] | Status |  | Rectified
T | Fencing | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
T1 | Is the fence of correct size and height? Please specify
T2 | Has the retaining wall been constructed to good workmanship standards?
T3 | Wire mesh tensioned.
T4 | Gate locking mechanism operational.
T5 | Gate operational and built as per specification. Indicate double or single gate.
T6 | Razor wire tension as per specification.
T7 | Razor wire mounting and support as per specification.
T8 | Is the bottom of fence and the retaining wall in parallel?
T9 | Are Gateposts sturdy and plumb?
T10 | Is the gate entry ramp acceptable?
T11 | Has all damaged galvanized areas been treated with Cold Galv
T12 | Are gates painted to specification?
T13 | Is fence painted to specification?
T14 | General workmanship
| TOWER, PLINTHS & FENCE |  |  |  |  | Status |  | Rectified
U | Service Entries | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
U1 | Service manholes built to specification.
U2 | Service entries are sealed as per specification.
U3 | General workmanship
Additional Comments
Main Contractor Representative
Names:
Sign:
Date:
This documentation is not intended for usage during site construction since a complete and more comprehensive documentation is available for such inspections. The above data is an extract from such document and is intended only for the assistance in identification of faults by the QA team of the main civil Site Contractor
| ROAD & SITE PREPARATION |  |  |  |  | Status |  | Rectified
V | Access Road and Site | Yes | No | Observation and Action |  | Pass | Fail | Yes | No
V1 | What Type of Access road has been supplied?
V2 | Is the Road supplied suitable for the purpose?
V3 | Does the access road allow for adequate storm water drainage?
V4 | Is the surface dressed?
V5 | Specify Base course?
V6 | Specify Asphalt thickness?
V7 | Is the Quality of General workmanship acceptable?
V8 | Is granite chippings applied? State Size.
V9 | Is drainage outlet provided at 3m intervals along the road?
V10 | General Workmanship.
Additional Comments
Main Contractor Representative
Names:
Sign:
Date:
This documentation is not intended for usage during site construction since a complete and more comprehensive documentation is available for such inspections. The above data is an extract from such document and is intended only for the assistance in identification of faults by the QA team of the main civil Site Contractor